Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Brazed-plate, double wall construction domestic-water heat exchangers.

SUBMITTALS

Product Data:  Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Retain paragraph below if equipment includes wiring.

Shop Drawings:

Wiring Diagrams:  For power, signal, and control wiring.

Plans, elevations, sectional and other details.

INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Sections specifying mechanical vibration, supports, and seismic controls.  See ASCE/SEI 7 for certification requirements for equipment and components.

Retain first paragraph below for product certificates from manufacturers.

Product Certificates:  For each type of, domestic-water heat exchanger, from manufacturer.

Retain first paragraph below if plumbing codes for Project area require domestic-water heat exchangers to be independent-testing-agency certified.  Verify availability for units retained.

Domestic-Water, Heat-Exchanger Labeling:  Certified and labeled by testing agency acceptable to authorities having jurisdiction.

Source quality-control reports.

Field quality-control reports.

Warranty:  Standard warranty specified in this specification.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:  For domestic-water heat exchangers to include in emergency, operation, and maintenance manuals.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  UL certified control panel and NEMA 4X rated control panel enclosure.

LEED-NC Prerequisite EA 2 requires that domestic-water heat exchangers comply with ASHRAE/IESNA 90.1, including equipment efficiency indicated in table titled "Performance Requirements for Water Heating Equipment."

ASME Compliance:  Where ASME-code construction is indicated, fabricate and label heat-exchanger to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1.

Lead Content:  Use low lead under 0.25% content of total system or lead free materials of construction for surfaces that are in contact with domestic water.

AHRI 400: Use heat exchanger certified by AHRI Liquid to Liquid Brazed and Fusion Bonded Plate Heat Exchangers (LLBF) certification program, based on AHRI Standard 400.

COORDINATION

Coordinate sizes and locations of concrete bases with actual equipment provided.

WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Standard Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of domestic-water heat exchangers that fail in materials or workmanship within specified warranty period.

Warranty Period:

Heat Exchanger shall carry a non-prorated (24) months warranty from date of shipment.

ALL OTHER COMPONENTS shall carry a non-prorated (1) year warranty.

PRODUCTS

See discussions on various types of domestic-water heat exchangers in the Evaluations for minimum and maximum limits on capacity and recovery of domestic-water heat exchangers in this Section.

Vitraglas and Hydrojet are trademarks of Bradford White Corporation.

PLATE, DOMESTIC-WATER HEAT EXCHANGERS

Domestic-water heat exchangers in this article do not have controls.  Control valves and devices are specified in heating-fluid piping Sections.

Brazed-Plate, Domestic-Water Heat Exchangers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Basis-of-Design Product: Subject to compliance with requirements, provide product indicated on Drawings Diversified Heat Transfer Inc. (DHT); SuperPlate Model SPB-____D or comparable product by one of the following:

Diversified Heat Transfer Inc. (DHT)

_____________________

_____________________

Description:  Assembly of heat-exchanger plates, permanently brazed together, for using heating hot water to heat domestic water.

          - Working-Pressure Rating:  Packaged heater shall be rated for 150 psig minimum at 250°F.

          - Plate Construction: Double wall.

          - Plate Material: 316L Stainless steel plates.

          - Plate Thickness:  Not less than 0.024 inch (0.6 mm) combined.

          - Brazing Filler Metal: Copper.

          - Heat Exchanger Connections:

2 inches (DN 50) and 2-1/2 inches (DN 65): Victaulic.

          - AHRI 400: Use heat exchanger certified based on AHRI Standard 400.

          - KIWA certification: Use KIWA certified double wall Brazed-plate heat exchanger.

        - SKID PACKAGE CONSTRUCTION AND CONTROLS:

          - Temperature Control:  Include adjustable temperature solid-state control module, mounted externally on heat exchanger skid. Control panel temperature set point range shall be from minimum 32°F to maximum 190°F. Unit shall include modulating 3-way electronic control valve to maintain hot water supply temperature within +/-4 deg F variation from set point when operated under normal load conditions with maximum load variation up to 25% of heating capacity.

Safety Control:

Include automatic, over-temperature-limit function which shall close the control valve in over temperature condition.

Include sound alarm functionality in the safety controls. Red light shall turn on when hot water temperature reaches alarm setting and alarm shall start sounding. In the next step, controller shall interrupt power supply to the control valve causing it to close. When unit goes back to normal operating temperature conditions, green light shall turn on but the siren should continue until owner manually presses the switch to turn it off and the power to control valve shall restore.

Relief Valves:  ASME rated and stamped for combination temperature-and-pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input. Relief valve shall confirm ANSI Z21.22 with relieving capacity of at least as heat input, and set at 150 PSIG/210°F.

Miscellaneous Components: Factory fabricated skid package with single point piping connections to produce domestic hot water using heating hot water.

Boiler water inlet piping manifold shall include isolation valve, strainer with dirt gauge and drain valve. Boiler outlet piping manifold shall include 3-way control valve and an isolation valve. Bypass piping shall include an isolation valve.

Control valve shall have magnetic actuator with fail-close design or loss of power and fast position time of less than 2 seconds. Control valve shall have tight shut-off with low leakage of max 0.02% of Cv value, high rangeability, 1000 to 1 turndown and equal percentage valve characteristic.

Domestic water inlet stainless steel piping manifold shall include strainer and an isolation valve. Recirculation piping to include constant speed recirculation pump and domestic hot water supply piping shall include pressure gage, thermometer, relief valve, isolation valve and drain valve.

End Connections for field piping: Threaded standard NPS 1-1/2 (DN40) up to 2-1/2 inches (DN 65).

Circulating Pump:  UL/CUL listed, lead-free bronze and/or stainless steel material construction, in-line pump. Include mechanical seals, 150-psig maximum working-pressure rating, and 225 deg F continuous-water-temperature rating.

Pump Control: Constant speed pump wired for continuous operation and re-circulate water in the heat exchanger from hot water discharge to cold water inlet side.

Control Panel shall be provided with the following associated features:

Factory mounted on the skid package. Provide manual disconnect switch for power supply to control panel and refer to electrical drawings/specifications and codes for details.

Control Panel shall have password protection.

Heater shall be supplied with solid-state control module with LCD backlit LED display and LED pilot lights to indicate on; off, primary high limit, and secondary high limit.

Solid-state control module shall be provided with a field programmable digital electronic PID controller allowing the user to set operating and temperature limits on the display screen.

Solid –state control module shall be supplied with dry contact closure outputs to indicate to building management system (BMS) the occurrence of power on, primary high temperature, and secondary high temperature.

Control module shall be supplied with an on-off switch and shall be mounted in a NEMA 4 panel; all solenoids and limits shall be 24 VAC.

Building Management System Interface:  The control panel either shall or shall not be capable of remote communications with the building management system to:

Turn the heater on or off through a remote relay suitable for 24 VAC (1amp).

Remotely set the temperature of the heater using 4-20mA input signal.

Remotely monitor the operating temperature.

Remotely monitor over temperature alarm.

Remotely monitor control valve opening percentage.

For Interface with BACnet TCP/IP, BACnet MS/TP, LonWorks, Metasys N2 and Modbus TCP/IP protocols; an external Diversified Heat Transfer supplied built-in translation communications gateway shall be utilized.

Stand:  Factory fabricated and powder coated support frames and base skid for floor mounting.

If more than one plate, domestic-water heat exchanger is required on Project, delete paragraph below and schedule plate, domestic-water heat exchangers on Drawings.

Capacity and Characteristics:

Number of Plates:             .

Recovery:          gph at          deg F temperature rise.

Domestic-Water Piping Size:             .

Domestic-Water Temperature Setting:           deg F.

Retain one of first two subparagraphs below.

Heating Hot-Water Supply:

Inlet Temperature:           deg F.

Outlet Temperature:           deg F.

Pipe Size:             .

EXECUTION

DOMESTIC-WATER, HEAT-EXCHANGER INSTALLATION

Domestic-Water, Heat-Exchanger Mounting:  Install domestic-water heat exchangers on concrete base.  Comply with requirements for concrete bases specified in Section 033000 "Cast-in-Place Concrete." Section 033053 "Miscellaneous Cast-in-Place Concrete."

Install domestic-water heat exchangers level and plumb, according to layout drawings, original design, and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

Install shutoff valves on domestic-water-supply piping to heat exchangers and on domestic-hot-water outlet piping.  Comply with requirements for shutoff valves specified in Section 220523 "General-Duty Valves for Plumbing Piping."

Install shutoff valves on heating hot-water piping to heat exchangers.  Comply with requirements for shutoff valves specified in Section 230523 "General-Duty Valves for HVAC Piping."

Install shutoff valves on steam and condensate piping to heat exchangers.  Comply with requirements for shutoff valves specified in Section 230523 "General-Duty Valves for HVAC Piping."

Retain first paragraph below if domestic-water heat exchangers are required to withstand seismic design loads.  Insert special requirements for seismic restraints here or detail on Drawings.

Install domestic-water heat exchangers with seismic-restraint devices.  Comply with requirements for seismic-restraint devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

Install temperature and pressure relief valves in top portion of storage-tank shells of domestic-water heat exchangers with domestic-water storage.  Use relief valves with sensing elements that extend into shells.  Extend relief-valve outlet, with drain piping same as domestic-water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

Install combination temperature and pressure relief valves in water piping for domestic-water heat exchangers without storage.  Extend relief-valve outlet, with drain piping same as domestic-water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

Install heat-exchanger drain piping as indirect waste to spill by positive air gap into open drains or over floor drains.  Install hose-end drain valves at low points in water piping for domestic-water heat exchangers that do not have tank drains.  Comply with requirements for hose-end drain valves specified in Section 221119 "Domestic Water Piping Specialties."

Install thermometer on each domestic-water, heat-exchanger,[ inlet and] outlet piping, and install thermometer on each domestic-water, heat-exchanger, heating-fluid[ inlet and] outlet piping.  Comply with requirements for thermometers specified in Section 220519 "Meters and Gages for Plumbing Piping."

Install pressure gages on domestic-water, heat-exchanger, heating-fluid piping.  Comply with requirements for pressure gages specified in Section 220519 "Meters and Gages for Plumbing Piping."

Fill domestic-water heat exchangers with water.

Charge domestic-water compression tanks with air.

CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Comply with requirements for piping specified in Section 221116 "Domestic Water Piping."

Comply with requirements for heating hot-water piping specified in Section 232113 "Hydronic Piping" and Section 232116 Hydronic Piping Specialties."

Drawings indicate general arrangement of piping, fittings, and specialties.

Where installing piping adjacent to domestic-water heat exchangers, allow space for service and maintenance of heat exchangers.  Arrange piping for easy removal of domestic-water heat exchangers.

IDENTIFICATION

Identify system components.  Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

FIELD QUALITY CONTROL

Perform tests and inspections.

Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper operation.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Domestic-water heat exchangers will be considered defective if they do not pass tests and inspections.  Comply with requirements in Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Prepare test and inspection reports.

DEMONSTRATION

Train Owner's maintenance personnel to adjust, operate, and maintain domestic-water heat exchangers.

END OF SECTION