Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Circulating, storage, brazed-plate domestic-water heat exchangers utilizing hot water as the energy source.

SUBMITTALS

Product Data:  Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Retain paragraph below if equipment includes wiring.

Shop Drawings:

Wiring Diagrams:  For power, signal, and control wiring.

Plan, elevations, sectional and other details.

INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Sections specifying mechanical vibration, supports, and seismic controls.  See ASCE/SEI 7 for certification requirements for equipment and components.

Retain first paragraph below for product certificates from manufacturers.

Product Certificates:  For each type of circulating, domestic-water storage heat exchanger, from manufacturer.

Retain first paragraph below if plumbing codes for Project area require domestic-water heat exchangers to be independent-testing-agency certified.  Verify availability for units retained.

Domestic-Water, Heat-Exchanger Labeling:  Certified and labeled by testing agency acceptable to authorities having jurisdiction.

Source quality-control reports.

Field quality-control reports.

Warranty:  Sample of special warranty.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:  For domestic-water heat exchangers to include in emergency, operation, and maintenance manuals.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application. Installed inside NEMA 4X rated control panel enclosure.

LEED-NC Prerequisite EA 2 requires that domestic-water heat exchangers comply with ASHRAE/IESNA 90.1, including equipment efficiency indicated in table titled "Performance Requirements for Water Heating Equipment."

ASHRAE/IESNA 90.1 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1.

ASME Compliance:  Where ASME-code construction is indicated, fabricate and label heat-exchanger to comply with ASME Boiler and Pressure Vessel Code:  Section VIII, Division 1 and storage tanks to comply with ASME Boiler and Pressure Vessel Code: Section IV, part HLW.

Lead Content:  Use low lead under 0.25% content of total system or lead free materials of construction for surfaces that are in contact with domestic water.

AHRI 400:  Use heat exchanger certified by AHRI Liquid to Liquid Brazed and Fusion Bonded Plate Heat Exchangers (LLBF) certification program, based on AHRI Standard 400.

COORDINATION

Coordinate sizes and locations of concrete bases with actual equipment provided.

WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Standard Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of domestic-water heat exchangers that fail in materials or workmanship within specified warranty period.

Warranty Period:

              - HEAT EXCHANGER(S) shall carry a non-prorated (5) year warranty.

              - STORAGE TANK shall carry a non-prorated warranty by one of the following:

Ten (10) year limited warranty on carbon steel tank with double glass lining.

Fifteen (15) year limited warranty on duplex stainless steel tank.

              - ALL OTHER COMPONENTS shall carry a non-prorated one (1) year warranty.

PRODUCTS

See discussions on various types of domestic-water heat exchangers in the Evaluations for minimum and maximum limits on capacity and recovery of domestic-water heat exchangers in this Section.

Vitraglas and Hydrojet are trademarks of Bradford White Corporation.

If more than one shell-and-tube, domestic-water heat exchanger is required on Project, delete paragraph below and schedule shell-and-tube, domestic-water heat exchangers on Drawings.

CIRCULATING, STORAGE, DOMESTIC-WATER HEAT EXCHANGERS

Circulating, Storage, Brazed-Plate, Domestic-Water Heat Exchangers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings Diversified Heat transfer Inc. (DHT); STP Series Model STP-____-____ or comparable product by one of the following:

Diversified Heat Transfer Inc. (DHT)

_____________________

_____________________

Description:  Packaged, large-capacity, hot-water storage tank with [Simplex] or [Duplex] <insert option> brazed-plate heat-exchanger module; circulators; controls; and specialties for heating domestic water with heating hot water.

Retain one of first two subparagraphs below.

Flow Pattern:  Standard-flow arrangement, with water from bottom of storage tank circulated across heat-exchanger plates and returned to tank.  Include hot-water outlet located at top of tank and temperature sensitive switch in tank. Counter flow arrangement through each heat exchanger for efficient heat transfer.

Storage-Tank Construction:  ASME-code [Carbon Steel] or [Duplex Stainless Steel] <Insert material> with 150-psig working-pressure rating.  Include nozzle and head for heat-exchanger tube coil.

Configuration:  Vertical.

Manhole:  12 by 16 inches in sidewall of vertical storage-tank shell.

Tappings:  Factory fabricated of materials compatible with tank.  Attach tappings to tank before testing and labeling.

NPS 3 (DN 80) Threaded ends according to ASME B1.20.1.

Lining:  Carbon Steel material tanks must have double glass lining complying with NSF 61 barrier materials for potable-water tank linings, including extending lining into and through tank fittings and outlets.

Insulation:  Complying with ASHRAE/IESNA 90.1, unless otherwise indicated, and suitable for operating temperature.  Surround entire storage tank and nozzle except connections and controls.

Anode Rods:  Factory installed, magnesium.

Dispersion Tubes: installed on both cold and hot water inlet to prevent mixing of hot and cold water inside the tank.

Brazed-Plate, Heat-Exchanger: Assembly of heat-exchanger plates, permanently brazed together.

Working-Pressure Rating:  Heat-Exchanger plates, permanently brazed together shall be rated for 150 psig minimum at 250°F.

Plate Construction: Double wall.

Plate Material: 316L Stainless steel plates.

Plate Thickness:  Not less than 0.024 inch (0.6 mm) combined.

Brazing Filler Metal: Copper.

Heat Exchanger Connections: 2 inches (DN 50) Victaulic.

AHRI 400: Use heat exchanger certified by AHRI Liquid to Liquid Brazed and Fusion Bonded Plate Heat Exchangers (LLBF) certification program, based on AHRI Standard 400.

KIWA certification: Use KIWA certified double wall Brazed-plate heat exchanger.

Temperature Control: Adjustable temperature aquastat, mounted in storage-tank shell wall unless otherwise indicated.

Relief Valves:  ASME rated and stamped for combination temperature-and-pressure relief valves.  Include one or more relief valves with total relieving capacity at least as great as heat input, and include pressure setting less than working-pressure rating of heat exchanger.  Select one relief valve with sensing element that extends into storage tank.

Circulating Pump:  UL/CUL listed, lead-free bronze and/or stainless steel material construction, in-line pump(s). Include mechanical seals, 150-psig maximum working-pressure rating, and 230 deg F continuous-water-temperature rating.

Aquastat to enable/disable the constant speed pump(s) to maintain water temperature inside tank.

Support:  Factory mounted on skids.

Control Panel shall be provided with the following associated features:

Factory mounted on the skid package. Provide manual disconnect switch for power supply to control panel and refer to electrical drawings/specifications and codes for details.

Normally open time delay relay to start/stop domestic circulator pump(s) and normally open relay contacts to start/stop boiler; limits shall be 120 VAC.

Control module shall be supplied with an on-off switch and shall be mounted in a NEMA 4X panel enclosure.

If more than one circulating, domestic-water heat exchanger is required on Project, delete paragraph below and schedule circulating, domestic-water heat exchangers on Drawings.

Capacity and Characteristics:

Capacity:  _____ gal.

Recovery:  _____ gph at ____ deg F temperature rise.

Domestic-Water Pipe Size:  3 NPS.

Hot-Water Temperature Setting:  _____ deg F.

Retain one of first two subparagraphs below.

Heating Hot-Water Supply:

Inlet Temperature:           deg F.

Outlet Temperature:           deg F.

Pipe Size:  _____

Retain first subparagraph below if retaining "Steam Supply" Subparagraph above.

Electrical Characteristics:

Volts:  _____

Phases:  _____

Hertz:  _____

Full-Load Amperes:  _____

Minimum Circuit Ampacity:  _____

Maximum Overcurrent Protection:  _____

SOURCE QUALITY CONTROL

Retain first paragraph below for factory-assembled, domestic-water heat exchangers.  Factory tests are an added cost option and may not be available from some manufacturers.  Verify requirement with Owner.

Factory Tests:  Test and inspect domestic-water heat exchangers specified to be ASME-code construction, according to ASME Boiler and Pressure Vessel Code.

Hydrostatically test domestic-water heat exchangers to minimum of one and one-half times pressure rating before shipment.

Domestic-water heat exchangers will be considered defective if they do not pass tests and inspections.  Comply with requirements in Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Prepare test and inspection reports.

EXECUTION

DOMESTIC-WATER, HEAT-EXCHANGER INSTALLATION

Domestic-Water, Heat-Exchanger Mounting:  Install domestic-water heat exchangers on concrete base.  Comply with requirements for concrete bases specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Install domestic-water heat exchangers level and plumb, according to layout drawings, original design, and referenced standards.  Maintain manufacturer's recommended clearances.  Arrange units so controls and devices needing service are accessible.

Install shutoff valves on domestic-water-supply piping to heat exchangers and on domestic-hot-water outlet piping.  Comply with requirements for shutoff valves specified in Section 220523 "General-Duty Valves for Plumbing Piping."

Install shutoff valves on heating hot-water piping to heat exchangers.  Comply with requirements for shutoff valves specified in Section 230523 "General-Duty Valves for HVAC Piping."

Install shutoff valves on steam and condensate piping to heat exchangers.  Comply with requirements for shutoff valves specified in Section 230523 "General-Duty Valves for HVAC Piping."

Retain first paragraph below if domestic-water heat exchangers are required to withstand seismic design loads.  Insert special requirements for seismic restraints here or detail on Drawings.

Install domestic-water heat exchangers with seismic-restraint devices.  Comply with requirements for seismic-restraint devices specified in Section 220548 "Vibration and Seismic Controls for Plumbing Piping and Equipment."

Install temperature and pressure relief valves in top portion of storage-tank shells of domestic-water heat exchangers with domestic-water storage.  Use relief valves with sensing elements that extend into shells.  Extend relief-valve outlet, with drain piping same as domestic-water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

Install combination temperature-and-pressure relief valves in water piping for domestic-water heat exchangers without storage. Extend relief-valve outlet, with drain piping same as domestic-water piping in continuous downward pitch, and discharge by positive air gap onto closest floor drain.

Install heat-exchanger drain piping as indirect waste to spill by positive air gap into open drains or over floor drains.  Install hose-end drain valves at low points in water piping for domestic-water heat exchangers that do not have tank drains.  Comply with requirements for hose-end drain valves specified in Section 221119 "Domestic Water Piping Specialties."

Install thermometer on each domestic-water, heat-exchanger, [inlet and] outlet piping, and install thermometer on each domestic-water, heat-exchanger, heating-fluid [inlet and] outlet piping.  Comply with requirements for thermometers specified in Section 220519 "Meters and Gages for Plumbing Piping."

Install pressure gages on domestic-water, heat-exchanger, heating-fluid piping.  Comply with requirements for pressure gages specified in Section 220519 "Meters and Gages for Plumbing Piping."

Fill domestic-water heat exchangers with water.

Charge domestic-water compression tanks with air.

CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Comply with requirements for piping specified in Section 221116 "Domestic Water Piping."

Comply with requirements for heating hot-water piping specified in Section 232113 "Hydronic Piping" and Section 232116 Hydronic Piping Specialties."

Drawings indicate general arrangement of piping, fittings, and specialties.

Where installing piping adjacent to domestic-water heat exchangers, allow space for service and maintenance of heat exchangers.  Arrange piping for easy removal of domestic-water heat exchangers.

IDENTIFICATION

Identify system components.  Comply with requirements for identification specified in Section 220553 "Identification for Plumbing Piping and Equipment."

FIELD QUALITY CONTROL

Perform tests and inspections.

Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper operation.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Domestic-water heat exchangers will be considered defective if they do not pass tests and inspections.  Comply with requirements in Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Prepare test and inspection reports.

DEMONSTRATION

Train Owner's maintenance personnel to adjust, operate, and maintain domestic water heaters.

END OF SECTION